## Structure
Summary structure
Energy & savings analysis |  |  |  | Report energy |  |  | Report safety | [5 empty] | Report maintenance | [5 empty] | Report others
Insulation | [10 empty] | Safety | [5 empty] | Maintenance | [5 empty] | Custom report
Non - insulated |  |  |  | Insulated |  |  |  | Cold |  |  | Hot Surface | Fire Protect. |  | Traffic | Housekeeping | Others | Damaged | Leakage | Condensation | Structural | Mechanical | Electrical | basic report
Surface & unknown | Pipe | Valve | Flanges | Insulated Surface & unknown | Insulated Pipe | Damaged |  | Energy | Damaged | Condensation |  | basic report |  | basic report | basic report | basic report |  |  |  | basic report | basic report | basic report
energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis |  |  | energy |  |  | energy | Report Safety |  | Report safety | Report safety | Report safety | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance

## Summary id
Summary structure
Energy & savings analysis |  |  |  | Report energy |  |  | Report safety | [5 empty] | Report maintenance | [5 empty] | Report others
Insulation | [10 empty] | Safety | [5 empty] | Maintenance | [5 empty] | Custom report
Non - insulated |  |  |  | Insulated |  |  |  | Cold |  |  | Hot Surface | Fire Protect. |  | Traffic | Housekeeping | Others | Damaged | Leakage | Condensation | Structural | Mechanical | Electrical | basic report
Surface & unknown | Pipe | Valve | Flanges | Insulated Surface & unknown | Insulated Pipe | Damaged |  | Energy | Damaged | Condensation |  | basic report |  | basic report | basic report | basic report |  |  |  | basic report | basic report | basic report
energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis | energy & saving analysis |  |  | energy |  |  | energy | Report Safety |  | Report safety | Report safety | Report safety | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance | report maintenance
Summary id | [10 empty] | Hot surface | Fire Protect |  | Traffic | Housekeeping | others | Damaged | Leakage | Condensation | Structural | Mechanical | Electrical | others

## TBi advise
Advise in the component screen (formulas 30, 31, 49, 50) | Summary | Surface | Pipe | Flange | Valve | Undefined | I Surface | I Pipe | I Undefined
System ok | OK | x | x | x | x |  | x | x
Insulation recommended | Recommended | x | x | x | x
SAFETY - Insulation recommended | Recommended | x | x | x | x | x | x | x | x
Total surface must be defined. Units per m² | Define total surface |  |  |  |  | x |  |  | x
Saving can be achieved …….. | ↑ Performance or thickness | [5 empty] | x | x
Maintenace

## Summary v5
|  |  | Energy & CO2 analysis per year |  |  |  |  | Safety | Maintenance | Others | TBi | Input
| Component / Location |  | Current Losses & Emissions |  | Potential savings | [5 empty] | TBi Advise | Insulated | Surface (m²) | Diameter (mm) | Length | Items number
[14 empty] | Dimension | Dimension
| 1.- | Tank roof 58 | 869.2 | kWh | 690 | -- 827,1 | MWh | Railing | Corroded |  |  | Y | 216
|  |  | 43443 | € | 40567 | -- 41.364 | €
|  |  | 2.7 | tn CO2 | 2.1 | -- 2,5 | tn CO2 | Add>> | Add>> | Add>>
| 2.- | Flange 234/240 | 24.3 | kWh | 21.5 | -- 23,2 | kWh | Hot surface | Leakage |  |  | N |  | 20 |  | 6
|  |  | 43443 | € | 40567 | -- 41.364 | €
|  |  | 2.7 | tn CO2 | 2.1 | -- 2,5 | tn CO2 | Add>> | Add>> | Add>>
| 4.- | Manhole 71 | 24.3 | kWh | 21.5 | -- 23,2 | kWh | Hot Surface |  |  |  | N
|  |  | 43443 | € | 40567 | -- 41.364 | €
|  |  | 2.7 | tn CO2 | 2.1 | -- 2,5 | tn CO2 | Housekeeping | Add>> | Add>>
|  | TOTAL PROJECT | 893.5 | MWh | 711.5 | -- 850,3 | kWh
|  |  | 43443 | € | 40567 | -- 41.364 | €
|  |  | 2.7 | tn CO2 | 2.1 | -- 2,5 | tn CO2
|  | 0.61 | 2.1 |  | 2.2 |  | 24.3 | 869.2
|  | 0.7 | 3 |  | 3 |  | 30 | 900
|  | 0.35 | 1.5 |  | 1.5 |  | 15 | 450
|  | 10446 | 6497 |  | 497 |  | 186 | 123
|  | 1870 | 489 |  | 89 |  | 38 | 26
|  | 427 | 220 |  | 20 |  | 9 | 6
|  | 11000 | 6500 |  | 500 |  | 190 | 130
|  | 1900 | 490 |  | 89 |  | 38 | 26
|  | 430 | 220 |  | 20 |  | 9 | 6
|  | 10446 | 6497 |  | 497 |  | 186 | 123
|  | 1870 | 489 |  | 89 |  | 38 | 26
|  | 427 | 220 |  | 20 |  | 9 | 6
LOSES |  | 10400 | 6400 |  | 490 |  | 180 | 120
BASIC |  | 1800 | 480 |  | 80 |  | 38 | 26
ECO |  | 430 | 220 |  | 20 |  | 9 | 6
Insulation expert

## Chart
Step 1 | Step 2 | Step 3
texto alineado with current
misma talla de letra que annual savving text from xxx€ to xxxx€
texto alineado with current
Current
210 €
basic
insulation
good
insulation
Savings
Annual
Consumption
Annual Saving Potential
From 170 € to 200 €
Annual
Saving
Click on Next to get the result
170€
200€
10€
40€

## TBi
Upload documents plotplan, PFS, control room, tech specsetc…
insert some general documentation, dimension tables, flanges, etc…
PROJECT | IPCOM | DATE | 2018-05-03
USER | Luis Lopez Brunner | ENERGY PRICE | 0.036 | €/kWh
|  | CO2 emissions | 202 | gr CO2 per kWh | there is a list of default values
DAMAGE INSULATION

## Project
Project name
| Energy price |  | €/kWh
| Project leader |  |  |  | email
| Energy Manager |  |  |  | email
| Maintenance Manager |  |  |  | email
| HSE Manager |  |  |  | email
Upload documents plotplan, PFS, control room, tech specsetc…
insert some general documentation, dimension tables, flanges, etc…
PROJECT |  | IPCOM |  | DATE |  | 2018-05-03
USER |  | Luis Lopez Brunner |  | ENERGY PRICE |  | 0.05 | €/kWh
|  |  |  | CO2 emissions |  | 202 | gr CO2 per kWh
DAMAGE INSULATION

## Intro
Insulation report | Safety report
Maintenance report | Custom report
DAMAGE INSULATION

## Selection
SURFACES | PIPES | FLANGES | VALVES | UNDEFINED
SURFACES | PIPES | UNDEFINED |  | DAMAGED
ENERGY | CONDENSATION | DAMAGED
DAMAGE INSULATION

## Safety report
Hot surface | Fire protection | Housekeeping
Traffic | any other safety issue
DAMAGE INSULATION

## Maintenance report
Damaged insulation /cladding | Structural | Ice blocks & wet surfaces
Leakage | Mechanical equipement | Electrical equipement
DAMAGE INSULATION

## basic report
Component / Location |  | tank roof 21
hvuyfutcubjbouihoubnonojb
DAMAGE INSULATION
basic report
End

## Surface
remove medium temp
Up to ten pictures
|  | Component / Location |  |  |  | tank roof |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760 |  |  |  | Making points & temperatures |  | add medium or surface temp
report (record ) and move to selection
|  | Surface |  |  | 10 |  | m2
[12 empty] | Heat loss |  | 210557.6567 |  | kWh/a
[14 empty] | 7580.0756 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 186642.8604 | 206259.618 | kWh/a
[14 empty] | 6719.143 | 7425.3462 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Medium or Surf Temp. |  |  | 150 |  | °C |  |  |  |  | Insulation recommended
See the different making point temperatures, or introduce themif there is no picture. Calcualte the average for calculations. Free input if there is no info
p1
|  | p2 |  |  |  | up to 10 |  | average of all the points recorded or open cell to write any value
p3
P4
Window help to calculate surfaces
a |  |  | Ø |  | Ø | *
b |  | or |  | or | h
h
*only wall
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | S Surface in m² |  | θse Medium/Surface temp | θa Amb temp | ε surface material | OT Op Time in hr | € Energy price €/kWh | gr CO2 emission per kWh | hr | hcv | hse | q W/m2 | Q kWh | Q € | Q tn CO2 emission | Savings
tank roof |  | 10 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 202 | 9.6749 | 8.8145 | 18.4894 | 2403.6262 | 210557.6567 | 7580.0756 | 42.5326 | kWh | € | tn CO2 emission
ref min |  | 10 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 202 | 9.6749 | 8.8145 | 18.4894 | 273 | 23914.7963 | 860.9327 | 4.8308 | 186642.8604 | 6719.143 | 37.7019
ref max |  | 10 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 202 | 9.6749 | 8.8145 | 18.4894 | 49.0644 | 4298.0387 | 154.7294 | 0.8682 | 206259.618 | 7425.3462 | 41.6644
|  |  |  | MIN | max | [6 empty] | q W/m2 |  | si gas
|  | θm |  | 102.5 | 95 | [8 empty] | 147390.3597 | 5306.0529 | 29.7729
|  | λm |  | 0.047382 | 0.046234 | [8 empty] | 23914.7963 | 860.9327 | 4.8308 | 123475.5634 | 4445.1203 | 24.9421 | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses
|  | λdes |  | 0.071072 | 0.069351 | [8 empty] | 4298.0387 | 154.7294 | 0.8682 | 143092.321 | 5151.3236 | 28.9046
|  | Insulation thickness, e |  | 0.03 | 0.18 | m
|  | Rse |  | 0.054085 | 0.054085 | value at higher temperature, conservative calculation | [5 empty] | Insulation recommended
|  | Rins |  | 0.42211 | 2.5955
|  | q ref-pb |  | 2352.8906 | max heat loss for a payback of predifined Cpb | max heat loss for a payback of predifined Cpb
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte, σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
| Cpb valve and flanges |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | Cpb=investment/payback
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
Assumptions
•Measured temperature is always lower than medium temperature – conservative
•Wind speed = 0 m/s – conservative
•Up to 300 °C
•Always turbulent - H^3Δθ>10
•Energy saving calculations based on only 20 mm or 50 mm insulation depending on Δθ, (internal number not known by the user). Two options:
§Lambda simulation (Ftot=1,5) and approximated calculation q | [10 empty] | Mineral wool 1.6.2b Pipe sections 50-80 kg/m³
(hse = un-ins hse - conservative),
§Fixed values based on calculations (surfaces emissivity 0,5)
• Δθ < 25°C (20mm) - 75 % HL saving
•25°C < Δθ < 100°C (20mm)- 80 % HL saving
•100°C < Δθ (50mm) - 90 % HL saving
•Recommendation – safety first , two options
• based on payback calculation 5years and 80 €/m2 (internal number not known by the user)
•Fixed values depending on Δθ
Component |  | S Surface in m² |  | θse Medium/Surface temp | θa Amb temp | ε surface material | OT Op Time in hr | € Energy price €/kWh | hr | hcv | hse | q W/m2 | Q kWh | Q € | Savings
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref min | [8 empty] | 1 | 2 | 3 | 20 | 5 | 6 | 26 | 28
ref max | [8 empty] | 1 | 2 | 3 | 21 | 5 | 6 | 27 | 29
|  |  |  | MIN | max | [6 empty] | q W/m2
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14 | m
|  | Rse |  | 15 | 16 | value at higher temperature, conservative calculation | [5 empty] | 30
|  | Rins |  | 17 | 18
|  | q ref-pb |  | 19 | max heat loss for a payback of predifined Cpb | max heat loss for a payback of predifined Cpb
DAMAGE INSULATION
DAMAGE INSULATION
Un insulated Surface
Comments
Space issue
Operational risk
Safety risk
End
New
TIPCHECK

## Pipe
|  | Component / Location |  |  | Burner /L6 | Pipe 2119 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
|  | Nominal Diameter (DN) | 150 |  |  | Length |  | 1 |  | m
[12 empty] | Heat loss |  | 9829.9404 |  | kWh/a
[14 empty] | 353.8779 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 7836.9268 | 9401.3395 | kWh/a
[14 empty] | 282.1294 | 338.4482 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Medium or Surf Temp. |  |  | 150 |  | °C |  |  |  |  | Insulation recommended
Component |  | DN | De (m) | Length (m) |  | θse Medium or Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
Pipe 2119 |  | 150 | 0.169 | 1 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 9.6749 | 0.62749 | 6.583 | 6.031 | 16.258 | 0.11585 | 1122.1393 | 9829.9404 | 353.8779 | kWh | €
ref min |  |  | 0.209 | 1 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 9.6749 | 1.1868 | 6.2425 | 6.031 | 15.9175 | 0.095682 | 227.513 | 1993.0136 | 71.7485 | 7836.9268 | 282.1294
ref max |  |  | 0.529 | 1 |  | 150 | 20 | 0.9 | 8760 | 0.036 | 9.6749 | 19.2447 | 4.9492 | 6.031 | 15.7059 | 0.038312 | 48.927 | 428.6009 | 15.4296 | 9401.3395 | 338.4482
|  |  |  | min | max | [11 empty] | q W/m |  | 1.9856
|  | θm |  | 102.5 | 95 | [13 empty] | 0.40259
|  | λm |  | 0.047382 | 0.046234 | [13 empty] | 0.086577 |  | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.071072 | 0.069351
|  | Insulation thickness, e |  | 0.02 | 0.18 | m
|  | D e,min/max | Dins | 0.209 | 0.529 | m
|  | Rins |  | 0.47571 | 2.6187 | [8 empty] | Insulation recommended
|  | ql ref-pb |  | 1088.8266 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 0.65659
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to communicate less
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Medium or Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql3 W/m | Q kWh | Q € | Savings
|  |  | default | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6 | kWh | €
ref min |  |  | 36 | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 44 | 6 | 26 | 28
ref max |  |  | 37 | [7 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 44 | 6 | 27 | 29
|  |  |  | min | max | [11 empty] | q W/m
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14 | m
|  | D e,min/max | Dins | 36 | 37 | m
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 41 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Un-insulated pipe
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK
back

## Flange
|  | Component / Location |  |  | Burner /L6 | Flange 2345 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
Bottom
0,5 is the deafault value
It opens a window where Equivalent length can be modify
Equivlent length decription: Default value for flanges 0,5 m Free input - xxxxx m
|  | Nominal Diameter (DN) | 80 |  |  | Items number |  | 6 | 0.5
[12 empty] | Heat loss |  | 24273.1278 |  | kWh/a
[14 empty] | 873.8326 |  | €/a
|  | Surface Material |  |  | Corroded |  | 0.8
[12 empty] | Saving potential |  | 21514.8009 | 23144.3019 | kWh/a
[14 empty] | 774.5328 | 833.1949 | €/a
|  | Ambient Temp. |  |  | 37 |  | °C
|  | Medium or Surf Temp. |  |  | 204 |  | °C |  |  |  |  | Insulation recommended
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
0 |  | 80 | 0.089 | 0.5 |  | 204 | 37 | 0.8 | 8760 | 0.036 | 6 | 11.5538 | 0.11773 | 8.227 | 6.5506 | 19.7808 | 0.18081 | 923.635 | 24273.1278 | 873.8326 | kWh | €
ref |  |  | 0.189 | 0.5 |  | 204 | 37 | 0.8 | 8760 | 0.036 | 6 | 11.5538 | 1.1275 | 6.8151 | 6.5506 | 18.3689 | 0.091686 | 104.9592 | 2758.3269 | 99.2998 | 21514.8009 | 774.5328
ref max |  |  | 0.589 | 0.5 |  | 204 | 37 | 0.8 | 8760 | 0.036 | 6 | 11.5538 | 34.1242 | 5.1293 | 6.5506 | 18.1044 | 0.02985 | 42.9538 | 1128.8259 | 40.6377 | 23144.3019 | 833.1949
|  |  |  | min | max
|  | θm |  | 138 | 130.5
|  | λm |  | 0.053293 | 0.051973 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.079939 | 0.077959
|  | Insulation thickness, e |  | 0.05 | 0.25
|  | D e,min/max | Dins | 0.189 | 0.589
|  | Rins |  | 1.4994 | 3.858 | [8 empty] | Insulation recommended
|  | ql ref-pb |  | 829.4946 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 0.59376
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to communicate less
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
|  |  | default | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 47 | 6 | kWh | €
ref min |  |  | De,min | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 47 | 6 | 26 | 28
ref max |  |  | De,max | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 47 | 6 | 27 | 29
|  |  |  | min | max
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14
|  | D e,min/max | Dins | 36 | 37
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 48 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Un-insulated flange
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK
back

## Valve
|  | Component / Location |  |  | Burner /L6 | Valve 20456 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
Bottom
1 is the deafault value
It opens a window where Equivalent length can be modify
Equivlent length decription: Default value for valves 1 m Free input - xxxxx m
|  | Nominal Diameter (DN) | 150 |  |  | Number of items |  | 5 | 1
[12 empty] | Heat loss |  | 89460.1444 |  | kWh/a
[14 empty] | 3220.5652 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 81028.9365 | 86524.31 | kWh/a
[14 empty] | 2917.0417 | 3114.8752 | €/a
|  | Ambient Temp. |  |  | 15 |  | °C
|  | Medium or Surf Temp. |  |  | 210 |  | °C |  |  |  |  | SAFETY-Insulation recommended
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
0 |  | 150 | 0.169 | 1 |  | 210 | 15 | 0.9 | 8760 | 0.036 | 5 | 12.4427 | 0.94123 | 7.2853 | 6.8944 | 19.728 | 0.095473 | 2042.469 | 89460.1444 | 3220.5652 | kWh | €
ref min |  |  | 0.269 | 1 |  | 210 | 15 | 0.9 | 8760 | 0.036 | 5 | 12.4427 | 3.7957 | 6.4861 | 6.8944 | 18.9288 | 0.062514 | 192.4933 | 8431.2079 | 303.5235 | 81028.9365 | 2917.0417
ref max |  |  | 0.669 | 1 |  | 210 | 15 | 0.9 | 8760 | 0.036 | 5 | 12.4427 | 58.3866 | 5.1649 | 6.8944 | 19.3371 | 0.024605 | 67.0282 | 2935.8344 | 105.69 | 86524.31 | 3114.8752
|  |  |  | min | max
|  | θm |  | 130 | 122.5
|  | λm |  | 0.051886 | 0.050608 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thickness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 0.077829 | 0.075912
|  | Insulation thickness |  | 0.05 | 0.25 | m
|  | D ins | Dins | 0.269 | 0.669 | m
|  | Rins |  | 0.95051 | 2.8846 | [8 empty] | SAFETY-Insulation recommended
|  | ql ref-pb |  | 1908.4808
|  | m2/m |  | 0.84509
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
Cpbf fitting |  |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years |  | Cpb=investment/payback
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | thers is an internal factor of 0,1 to hide price calcualtion backwards
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
DN | mm
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) |  | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | n number | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar turbulent | hcv H turbulent | hse | Rle | ql W/m | Q kWh | Q € | Savings
|  |  | default | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 47 | 6 | kWh | €
ref min |  |  | De,min | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 45 | 47 | 6 | 26 | 28
ref max |  |  | De,max | [8 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 46 | 47 | 6 | 27 | 29
|  |  |  | min | max
|  | θm |  | 7 | 8
|  | λm |  | 9 | 10 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses . Incresed of thiskness is integrated for Rsle but not for hse (small impact). Always conservative
|  | λdes |  | 11 | 12
|  | Insulation thickness, e |  | 13 | 14
|  | D e,min/max | Dins | 36 | 37
|  | Rins |  | 38 | 39 | [8 empty] | 30
|  | ql ref-pb |  | 48 |  | max heat loss for a payback of predifined Cpb, multiply for 10000 to pass to W and internal factor of 0,1
|  | m2/m, Sp |  | 40
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
back
Un-insulated valve
Comments
Space issue
Operational risk
Safety risk
End
TIPCHECK

## Unknow surface
|  | Component / Location |  |  | Connexion tank21 |  |  |  |  | Operational time |  |  | 6000 hours |  | 6000
1
[12 empty] | Heat loss |  | 3812.9247 |  | kWh/m²a |  |  |  | Same formulas than surface but with 1m2 by default
[14 empty] | 137.2653 |  | €/m²a
|  | Surface Material |  |  | Painted |  | 0.9
[12 empty] | Minimun Saving potential |  | 3104.6805 |  | kWh/m²a
[14 empty] | 111.7685 |  | €/m²a
|  | Ambient Temp. |  |  | 15 |  | °C
|  | Medium or Surf Temp. |  |  | 65 |  | °C |  |  |  |  | Potential savings per m² if insulated. Total surface must be defined
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings |  |  |  |  | Same formulas than surface but with 1m2 by default . Only min potential savings
Connexion tank21 |  | 1 | 0 | 65 | 15 | 0.9 | 6000 | 0.036 | 6.2995 | 6.4102 | 12.7097 | 635.4874 | 3812.9247 | 137.2653 | kWh | €
ref min |  | 1 | 0 | 65 | 15 | 0.9 | 6000 | 0.036 | 6.2995 | 6.4102 | 12.7097 | 118.0407 | 708.2442 | 25.4968 | 3104.6805 | 111.7685
q W/m2
|  | θm |  | 40
|  | λm |  | 0.038658 | [15 empty] | hse calculated with uninsulated temperature, higher temperature -> higher hse -> higher losses
|  | λdes |  | 0.057987
|  | Insulation thickness |  | 0.02 | m
|  | Rse |  | 0.07868 | value at higher temperature, conservative calculation | [6 empty] | Potential savings per m² if insulated. Total surface must be defined
|  | Rins |  | 0.3449 | [13 empty] | or | Insualtion will reduce the energy comsuption. A further analysis is needed to determine the total potential
|  | q ref-pb |  | 561.4134 | max heat loss for a payback of predifined Cpb | [13 empty] | Install insulation on surfaces at "medium temperature" °C leads to important energy savings
Default values for calcualtions | [19 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.5 |  |  | C | min mm | max mm
| a | 0.0338 |  | Δθ < | 80 | 20 | 100
| b | 0.0001173 |  | Δθ < | 150 | 30 | 180
| c | 7.545e-08 |  | Δθ < | 250 | 50 | 250
| d | 7.109e-10 |  | Δθ < |  | 80 | 300
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 250 | €/m2
| Cpb valve and flanges |  | 5 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6 |  |  | Cpb=investment/payback
[14 empty] | Coef for payback fitting - Cpbf |  |  | 5
Assumptions
Considering as a flat surface, conservative calculation for uninsulated and insulated
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
min | [8 empty] | 1 | 2 | 3 | 20 | 5 | 6 | 26 | 28
q W/m2
|  | θm |  | 7
|  | λm |  | 9
|  | λdes |  | 11
|  | Insulation thickness |  | 13 | m
|  | Rse |  | 15 | value at higher temperature, conservative calculation | [6 empty] | 31
|  | Rins |  | 17 | [13 empty] | or | Insualtion will reduce the energy comsuption. A further analysis is needed to determine the total potential
|  | q ref-pb |  | 19 | max heat loss for a payback of predifined Cpb | [13 empty] | Install insulation on surfaces at "medium temperature" °C leads to important energy savings
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
DAMAGE INSULATION
DAMAGE INSULATION
Un insulated Other
End
CHECK
back
Description

## I Surface
|  | Component / Location |  |  | Burner /L6 | Burner L6 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 200 |  | °C
|  | Surface |  |  | 10 |  | m2
[12 empty] | Heat loss |  | 57006.5118 |  | kWh/a
[14 empty] | 2052.2344 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 38498.5967 | 49122.5118 | kWh/a
[14 empty] | 1385.9495 | 1768.4104 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 70 |  | °C |  |  |  |  | "Savings can be achieved by increasing insulation performance or thickness"
[13 empty] | q3*op_time*surface | q3*op_time*surf*€ | saving |  | NOT TBi. Eiif table
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € |  |  | Insulation need in m
Burner L6 |  | 10 | 200 | 70 | 20 | 0.9 | 8760 | 0.036 | 6.605 | 6.4102 | 13.0152 | 650.7593 | 57006.5118 | 2052.2344 |  |  | 0.019977
ref | min | 10 | 200 | 55 | 35 | 0.8 | 8760 | 0.036 | 5.8408 | 4.7231 | 10.5639 | 211.2776 | 18507.9151 | 666.2849 |  |  | 0.06863
ref | max | 10 | 200 | 35 | 0.8 | 90 | 8760 | 0.036 |  |  |  | 90 | 7884 | 283.824 | kWh | € | 0.18333
[15 empty] | 38498.5967 | 1385.9495
[15 empty] | 49122.5118 | 1768.4104 | 0.1
W/mK
"Savings can be achieved by increasing insulation performance or thickness"
Default values for calcualtions | [17 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
ε ref = |  |  | 0.8
Max heat loss ref |  |  | 90 | W/M2
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q W/m2 | Q kWh | Q €
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref | min |  |  | default | default |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 26 | 28
ref | max | [10 empty] | default | 5 | 6 | 27 | 29
49
DAMAGE INSULATION
DAMAGE INSULATION
Insulated Surface
End
Comments
Space issue
Operational risk
Safety risk
TIPCHECK
back

## I Pipe
|  | Component / Location |  |  | Burner /L6 | Pipe preheater-burner |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 150 |  | °C
|  | External Diameter | 150 |  | mm | Length |  | 10 |  | m
[12 empty] | Heat loss |  | 20814.0487 |  | kWh/a
[14 empty] | 749.3058 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 11545.9827 | 12936.1926 | kWh/a
[14 empty] | 415.6554 | 465.7029 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 60 |  | °C |  |  |  |  | "Savings can be achieved by increasing the insulant performance or thickness"
[17 empty] | q=(θse-θa)/Rle |  |  | saving |  | NOT Tbi. Eiif table
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q € |  |  | Rl | Insulation need in m | Di
Pipe preheater-burner |  | 150 | 0.169 | 10 | 150 | 60 | 20 | 0.9 | 8760 | 0.036 | 6.2852 | 0.19307 | 4.9029 | 4.0876 | 11.1881 | 0.16835 | 237.6033 | 20814.0487 | 749.3058 |  |  | 0.37878 | 0.013249 | 0.1425
ref min |  |  | 0.169 | 10 | 150 | 55 | 35 | 0.8 | 8760 | 0.036 | 5.8408 | 0.096536 | 4.1228 | 3.2518 | 9.9636 | 0.18904 | 105.7998 | 9268.066 | 333.6504 |  |  | 0.89792 | 0.035499
ref max |  |  | 0.169 | 10 | 150 | 55 | 35 | [9 empty] | 89.9299 | 7877.8561 | 283.6028 | kWh | € | 1.0564 | 0.043393
[10 empty] | reference increasing thickness |  |  | 3.6705 | 3.2518 | 9.9636 | 0.11876 | 168.4033 |  |  | 11545.9827 | 415.6554
[20 empty] | 12936.1926 | 465.7029
[12 empty] | "Savings can be achieved by increasing the insulant performance or thickness" | [9 empty] | Conductivity
[22 empty] | Ft | 1.5
[22 empty] | a | 0.0338
[22 empty] | b | 0.0001173
Default values for calcualtions | [21 empty] | c | 7.545e-08
π |  |  | 3.1416 | [18 empty] | d | 7.109e-10
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
[22 empty] | 105 | 0.047771 | 0.071657
0.071657
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
Default value for ε = |  |  | 0.8
Ref max heat loss = |  |  | 85%
Increase thickness for Rls ref = |  |  | 0.05
Assumptions
For pipes system we calculate increasing performance of the insualtion system. | [8 empty] | For Rle ref , same De as component. If increaase insulation thickness , Rle will be lower and have more losses
DN | m
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q €
[11 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref min | [5 empty] | default | default |  |  |  | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref max | [10 empty] | 1 | 32 | 33 | 34 | 35 | 42 | default | 44 | 6 | kWh | €
[20 empty] | 26 | 28
[20 empty] | 27 | 29
49
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
back
TIPCHECK

## I surface cold
|  | Component / Location |  |  | Burner /L6 | Burner L6 |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 200 |  | °C
|  | Surface |  |  | 10 |  | m2
[12 empty] | Heat loss |  | 57006.5118 |  | kWh/a
[14 empty] | 2052.2344 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 11401.3024 | 31353.5815 | kWh/a
[14 empty] | 410.4469 | 1128.7289 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 70 |  | °C |  |  |  |  | "Savings can be achieved by increasing insulation performance or thickness"
[13 empty] | q3*op_time*surface | q3*op_time*surf*€ | saving |  | NOT TBi. Eiif table
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € |  |  | Insulation need in m
Burner L6 |  | 10 | 200 | 70 | 20 | 0.9 | 8760 | 0.036 | 6.605 | 6.4102 | 13.0152 | 650.7593 | 57006.5118 | 2052.2344 |  |  | 0.019977
ref | min | 10 | 200 | 55 | 35 | 0.8 | 8760 | 0.036 | 5.8408 | 4.7231 | 10.5639 | 520.6074 | 45605.2094 | 1641.7875 |  |  | 0.027852
ref | max | 10 | 200 | 35 | 0.8 | 90 | 8760 | 0.036 |  |  |  | 292.8417 | 25652.9303 | 923.5055 | kWh | € | 0.056344
[15 empty] | 11401.3024 | 410.4469
[15 empty] | 31353.5815 | 1128.7289 | 0.1
W/mK
"Savings can be achieved by increasing insulation performance or thickness"
Default values for calcualtions | [17 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
ε ref = |  |  | 0.8
Max heat loss ref |  |  | 90 | W/M2
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q W/m2 | Q kWh | Q €
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref | min |  |  | default | default |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 26 | 28
ref | max | [10 empty] | default | 5 | 6 | 27 | 29
49
DAMAGE INSULATION
DAMAGE INSULATION
Insulated Surface
End
Comments
Space issue
Operational risk
Safety risk
TIPCHECK
back

## I pipe cold
|  | Component / Location |  |  | Burner /L6 | Pipe preheater-burner |  |  |  | Operational time |  |  | 8760 hours (full year) |  | 8760
[10 empty] | Medium Temp. |  |  | 150 |  | °C
|  | External Diameter | 150 |  | mm | Length |  | 10 |  | m
[12 empty] | Heat loss |  | 20814.0487 |  | kWh/a
[14 empty] | 749.3058 |  | €/a
|  | Surface Material |  |  | Non metallic |  | 0.9
[12 empty] | Saving potential |  | 4162.8097 | 11447.7268 | kWh/a
[14 empty] | 149.8612 | 412.1182 | €/a
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 60 |  | °C |  |  |  |  | "Savings can be achieved by increasing the insulant performance or thickness"
[17 empty] | q=(θse-θa)/Rle |  |  | saving |  | NOT Tbi. Eiif table
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q € |  |  | Rl | Insulation need in m | Di
Pipe preheater-burner |  | 150 | 0.169 | 10 | 150 | 60 | 20 | 0.9 | 8760 | 0.036 | 6.2852 | 0.19307 | 4.9029 | 4.0876 | 11.1881 | 0.16835 | 237.6033 | 20814.0487 | 749.3058 |  |  | 0.37878 | 0.013249 | 0.1425
ref min |  |  | 0.169 | 10 | 150 | 55 | 35 | 0.8 | 8760 | 0.036 | 5.8408 | 0.096536 | 4.1228 | 3.2518 | 9.9636 | 0.18904 | 190.0826 | 16651.239 | 599.4446 |  |  | 0.49978 | 0.01798
ref max |  |  | 0.169 | 10 | 150 | 55 | 35 | [9 empty] | 106.9215 | 9366.3219 | 337.1876 | kWh | € | 0.8885 | 0.035047
[10 empty] | reference increasing thickness |  |  | 3.6705 | 3.2518 | 9.9636 | 0.11876 | 168.4033 |  |  | 4162.8097 | 149.8612
[20 empty] | 11447.7268 | 412.1182
[12 empty] | "Savings can be achieved by increasing the insulant performance or thickness" | [9 empty] | Conductivity
[22 empty] | Ft | 1.5
[22 empty] | a | 0.0338
[22 empty] | b | 0.0001173
Default values for calcualtions | [21 empty] | c | 7.545e-08
π |  |  | 3.1416 | [18 empty] | d | 7.109e-10
Boltzmann cte σ= |  |  | 5.6704e-08 |  |  |  |  | same default values as surface
[22 empty] | 105 | 0.047771 | 0.071657
0.071657
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
Default value for ε = |  |  | 0.8
Ref max heat loss = |  |  | 85%
Increase thickness for Rls ref = |  |  | 0.05
Assumptions
For pipes system we calculate increasing performance of the insualtion system. | [8 empty] | For Rle ref , same De as component. If increaase insulation thickness , Rle will be lower and have more losses
DN | m
10 | 0.018
15 | 0.022
20 | 0.027
25 | 0.034
32 | 0.043
40 | 0.049
50 | 0.061
60 | 0.072
65 | 0.077
80 | 0.089
100 | 0.115
125 | 0.141
150 | 0.169
200 | 0.22
250 | 0.273
300 | 0.324
350 | 0.356
400 | 0.407
450 | 0.458
500 | 0.508
600 | 0.61
700 | 0.712
800 | 0.813
900 | 0.915
1000 | 1.016
1100 | 1.12
1200 | 1.22
1400 | 1.42
1500 | 1.52
1600 | 1.62
1800 | 1.82
2000 | 2.02
2000 | 2.02
2200 | 2.22
2400 | 2.42
2600 | 2.62
2800 | 2.82
3000 | 3.02
3200 | 3.22
3400 | 3.42
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q €
[11 empty] | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref min | [5 empty] | default | default |  |  |  | 1 | 32 | 33 | 34 | 35 | 42 | 43 | 44 | 6
ref max | [10 empty] | 1 | 32 | 33 | 34 | 35 | 42 | default | 44 | 6 | kWh | €
[20 empty] | 26 | 28
[20 empty] | 27 | 29
49
Uninsulated pipe
Comments
Space issue
Operational risk
Safety risk
End
back
TIPCHECK

## Insulated Unknown surface
|  | Component / Location |  |  | Burner /L6 | N90323 |  |  |  | Operational time |  |  | 6000 hours |  | 6000
[10 empty] | Medium Temp. |  |  | 600 |  | °C
1
[12 empty] | Heat loss |  | 1772.9872 |  | kWh/m²/a
[14 empty] | 63.8275 |  | €/m²/a
|  | Surface Material |  |  | Painted |  | 0.9
[12 empty] | Minimun Saving potential |  | 505.3218 |  | kWh/m²/a
[14 empty] | 18.1916 |  | €/m²/a
|  | Ambient Temp. |  |  | 26 |  | °C
|  | Surface Temp. |  |  | 52 |  | °C |  |  |  |  | "Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined"
[13 empty] | q3*op_time*surface | q3*op_time*surf*€ | saving |  | NOT Tbi. Eiif table
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € |  |  | Insulation need in m
N90323 |  | 1 | 600 | 52 | 26 | 0.9 | 6000 | 0.036 | 6.2106 | 5.1547 | 11.3653 | 295.4979 | 1772.9872 | 63.8275 |  |  | 0.18545
ref | N90323 | 1 | 600 | 55 | 35 | 0.8 | 6000 | 0.036 | 5.8408 | 4.7231 | 10.5639 | 211.2776 | 1267.6654 | 45.636 |  |  | 0.25795
[15 empty] | kWh | € | 0.1
[15 empty] | 505.3218 | 18.1916 | W/mK
"Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined"
Default values for calcualtions | [17 empty] | Eiif default values - only access for Eiif , updated with new versions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
θse-θa for insulation recommendation | recommendation θse-θa |  | 25 | °C
| Cpb surface/pipe |  | 1.6
| Cpb valve and flanges |  | 2
Safety warning for θse> |  |  | 55 | °C
Criteria for Insulated, θse ref |  |  | 55
θa ref |  |  | 35
ε ref = |  |  | 0.8
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q €
[9 empty] | 1 | 2 | 3 | 4 | 5 | 6 | kWh | €
ref min |  |  |  | default | default |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 26 | 28
Potential savings per m² if increase of insulation preformance or thickness . Total surface must be defined
DAMAGE INSULATION
DAMAGE INSULATION
Insulated Surface
End
Comments
Space issue
Operational risk
Safety risk
CHECK
back
Description

## Cold Insulated
If Insulated
If surface temperature < ambient temperature
R46=R45*0,8 (en el excel del insualted surface or pipe)
R47=R45*0,45 (en el excel del insualted surface or pipe)
Component |  | DN | De (m) | Length (m) | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | Laminar /turbulent Laminar free cv De^3Δθ<10 | hcv H laminar | hcv H turbulent | hse | Rle | ql3 W/l | Q kWh | Q €
aaaaa |  | 100 | 100 | 1 | 120 | 10 | 20 | 0.9 | 8760 | 0.05 | 4.9082 | 0.031938 | 4.5951 | 3.3046 | 9.5033 | 0.29126 | 72.1011 | 631.6061 | 31.5803
ref min |  |  |  | 1 |  |  |  |  | 8760 | 0.05 | [6 empty] | 57.6809 | 505.2849 | 25.2642
ref max |  |  |  | 1 |  |  |  |  | 8760 | 0.05 | [6 empty] | 36.0506 | 315.803 | 15.7902 | kWh | €
[20 empty] | 126.3212 | 6.3161
[20 empty] | 315.803 | 15.7902

## Damaged
Seleccionar si la dimension principal es en m² o es una surficie curva dada en diametro exterior y longitud
Si se selecciona damaged cladding, aparecen estas opciones, igual para damaged insualtion
[6 empty] | Cladding | Insulation
[6 empty] | Lack of cladding | Lack of insualtion
[6 empty] | Foot traffic/Dent | Wet insulation
[6 empty] | Highly corroded | Old insualtion
[6 empty] | Others | Others
add a comment depending on the selection
add a comment depending on the selection
Damaged cladding
| General Stament |  | --> Cladding holds insualtion in place an protect it from external agents ensuring its performance
| Lack of cladding |  | --> The insulation is not protected anymore, water or other agent could get in
| Foot trafic |  | --> There is a reduction of the insulation thickness, higher energy conmsuption. The system is not watertight anhmore
| Highy corroded |  | --> Probably, there is a leak above in the system. Jacketing as a protecting layer gets weaker.
https://insulation.org/io/articles/maintain-insulation-jacketing-to-ensure-mechanical-insulation-performance/
Insulation
|  | General Stament |  | --> Any damage in the insulant leads to reduce its thermal performance and to increase the energy consumption
|  | Lack of insulation |  | --> A lack of insulation in a system means an easy way out/in for the heat increasing the energy consumption
|  | Wet insulation |  | --> Moisture inside the insulation structure can reduce the thermal performance up to 50% and increase the risk of CUI
|  | Old insulation |  | --> Heat cycles and external condition changes affect the estructure of the insulant reducing its performance
Damaged
Siempre visible "Insulation in cold systems is critical not only for energy efficiency but for safety and process requirements
Siempre visible if damaged cladding is selected "Cladding holds insualtion in place an protect it from external agents ensuring its performance"
Siempre visible if damaged insualtion is selected "Any damage in the insulant leads to reduce its thermal performance and to increase the energy consumption"

## Energy
|  | SURFACES |  |  | PIPES |  |  | FLANGES |  |  | VALVES |  |  | UNDEFINED
|  | SURFACES |  |  | PIPES |  |  | UNDEFINED
1.Heat gain instead of Heat loss
2 Add risk of condensation on the surface (maintenance report)
3 No potential saving information for insulated systems
For insulated systems, general statement: any failure in the insulated system can lead to condensations and increase of energy consumption
|  | Component / Location |  |  | Burner /L6 | hikhjkl |  |  |  | Operational time |  |  | 5000 hours |  | 5000
[10 empty] | Medium Temp. |  |  | 19 |  | °C
If there is no info about medium, take surface by default
|  | Surface |  |  | 100 |  | m2
|  | Surface Material |  |  | Corroded ε=0,8 |  | #N/A
[14 empty] | #N/A |  | #N/A
[14 empty] | #N/A |  | #N/A
|  | Ambient Temp. |  |  | 20 |  | °C
|  | Surface Temp. |  |  | 19 |  | °C |  |  |  |  | 0
[13 empty] | q3*op_time*surface | q3*op_time*surf*€
Component |  | Surface in m² | θi Medium temp | θse Surface temp | θa Amb temp | ε | Op Time in hr | Energy price €/kWh | hr | hcv turbulent | hse | q3 W/m2 | Q kWh | Q € | Savings |  |  |  |  | hr | hcv turbulent | hse | q3 W/m2
hikhjkl |  | 100 | 19 | 19 | 20 | #N/A | 5000 | 0.036 | #N/A | 1.74 | #N/A | #N/A | #N/A | #N/A | kWh | € |  |  |  | 4.5876 | 1.74 | 6.3276 | 6.3276
ref |  | 100 | 19 | 19 | 20 | #N/A | 5000 | 0.036 | #N/A | 1.74 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  | 4.5876 | 1.74 | 6.3276 | 1.7167
q W/m2
|  | θm |  | 19.5
|  | λm |  | 0.036121
|  | λdes |  | 0.046958
|  | Insulation thickness |  | 0.02 | m
|  | Rse |  | #N/A | value at higher temperature, conservative calculation | [6 empty] | #N/A
|  | Rins |  | 0.42592
|  | q ref-pb |  | #N/A | max heat loss for a payback of predifined Cpb
Default values for calcualtions
π |  |  | 3.1416
Boltzmann cte σ= |  |  | 5.6704e-08
| Conductivity |  |  | thickness selection
| Ft | 1.3 |  |  | C | mm
| a | 0.0338 |  | Δθ < | 80 | 20
| b | 0.0001173 |  | Δθ < | 150 | 50
| c | 7.545e-08 |  | Δθ < | 250 | 80
| d | 7.109e-10 |  | Δθ < |  | 100
It is not part of Tbi tool. It is an external eiif table
[14 empty] | Insulation cost surface /pipe |  |  | 80 | €/m2
| Cpb surface/pipe |  | 1.6 | [10 empty] | Insualtion cost matresses |  |  | 150 | €/unit
| Cpb valve and flanges |  | 3 | [10 empty] | Ref Payback time |  |  | 5 | years
Safety warning for θse> |  |  | 55 | °C | [9 empty] | Corf payback cal surface/pipe - Cpb |  |  | 1.6
[14 empty] | Coef for payback fitting - Cpbf |  |  | 3
DAMAGE INSULATION
Un insulated Surface
Comments
Space issue
Operational risk
Safety risk
End
New
CALCULATE

## Condensation
https://insulation.org/io/articles/maintain-insulation-jacketing-to-ensure-mechanical-insulation-performance/
Solo warning si el nombre no se rellena. El resto no es obligatorio
Medium
Siempre visible "Insulation in cold systems is critical not only for energy efficiency but for safety and process requirements
Se activa cuando se seleccion "Ice block indicates the failure of the insulation system (or the lack of it). A part from the potential energy savings, its weight represents a risk for the installation break down"
Se activa cuando se seleccion "Condensations indicates the need of a better insulation solution to bring the surface temperature above the dew point"
Siempre visible "Insulation in cold systems is critical not only for energy efficiency but for safety and process requirements
Siempre visible "Insulation in cold systems is critical not only for energy efficiency but for safety and process requirements
Condensation

## Leakage
Component / Location |  | Operational time | 5000 hours | #N/A
Medium
|  | Medium Temp. | 0 | °C
Leakage -urgent to fix
DAMAGE INSULATION
Leakage
End

## Summary default values
Material Surface - emissivity ε= |  | Coeficients |  |  |  |  | DN | m
Text | value | Cpb surface/pipe | 1.6 |  |  |  | 10 | 0.018
Defaul value | 0.8 | Cpb valve and flanges | 5 |  |  |  | 15 | 0.022
Metallic bright | 0.3 | [5 empty] | 20 | 0.027
Metallic | 0.6 | thickness selection |  |  |  |  | 25 | 0.034
Corroded | 0.8 |  | °C | min mm | max mm |  | 32 | 0.043
Painted | 0.9 | Δθ < | 80 | 20 | 100 |  | 40 | 0.049
Non metallic | 0.9 | Δθ < | 150 | 30 | 180 |  | 50 | 0.061
Free input | ---- | Δθ < | 250 | 50 | 250 |  | 60 | 0.072
|  | Δθ < |  | 80 | 300 |  | 65 | 0.077
Operational time | [6 empty] | 80 | 0.089
Text | value | Conductivity |  |  |  |  | 100 | 0.115
1000 hours | 1000 | Ft | 1.5 |  |  |  | 125 | 0.141
2000 hours | 2000 | a | 0.0338 |  |  |  | 150 | 0.169
3000 hours | 3000 | b | 0.0001173 |  |  |  | 200 | 0.22
4380 hours (1/2 year) | 4380 | c | 7.545e-08 |  | https://www.eia.gov/tools/faqs/faq.php?id=73&t=11 |  | 250 | 0.273
5000 hours | 5000 | d | 7.109e-10 |  |  |  | 300 | 0.324
6000 hours | 6000 | [5 empty] | 350 | 0.356
7000 hours | 7000 | [5 empty] | 400 | 0.407
8760 hours (full year) | 8760 |  |  |  | pound/MBtu |  | 450 | 0.458
free input | [6 empty] | 500 | 0.508
[7 empty] | 600 | 0.61
[7 empty] | 700 | 0.712
Number or constants |  | CO2 emissions | gr/kWh |  |  |  | 800 | 0.813
π | 3.1416 | Coal anthracite - eia | 354.33 | 228.6 |  |  | 900 | 0.915
Boltzmann cte σ= | 5.6704e-08 | Coal bituminous - eia | 318.835 | 205.7 |  |  | 1000 | 1.016
Safety warning for θse> | 55 | Coal lignite - eia | 333.87 | 215.4 |  |  | 1100 | 1.12
Criteria for Insulated, θse ref | 55 | Diesel - eia | 250.015 | 161.3 |  |  | 1200 | 1.22
Criteria for Insulated, θa ref | 35 | Gasoline - eia | 243.66 | 157.2 |  |  | 1400 | 1.42
ε ref = | 0.8 | Propane - eia | 215.45 | 139 |  |  | 1500 | 1.52
Max heat loss ref | 90 | Natural gas - eia | 181.35 | 117 |  |  | 1600 | 1.62
Criteria for Insulated, Ref max heat loss = | 0.85 | Coal import - VDI 4610 | 342 |  | 1.55 | 1 pound/Btu (th) = 1548757.170172 gram/kilowatt-hour | 1800 | 1.82
Safety warning for cold θse< | 0 | Brown coal dust - VDI 4610 | 353 |  |  | https://www.translatorscafe.com/unit-converter/en/fuel-efficiency-mass/5-15/Btu%20(IT)%2Fpound-gram%2Fkilowatt-hour/ | 2000 | 2.02
|  | Coal Rheinland- VDI 4610 | 410 |  |  |  | 2000 | 2.02
|  | Heavy fuel oil - VDI 4610 | 381 |  |  |  | 2200 | 2.22
|  | Natural gas - VDI 4610 | 202 |  |  |  | 2400 | 2.42
[7 empty] | 2600 | 2.62
[7 empty] | 2800 | 2.82
[7 empty] | 3000 | 3.02
[7 empty] | 3200 | 3.22
[7 empty] | 3400 | 3.42

## Default values
emissivity |  | operation hours |  | Safety risk
Defaul value | 0.8 | 1000 hours | 1000 | hot surface
Metallic bright | 0.3 | 2000 hours | 2000 | fire protection
Metallic | 0.6 | 3000 hours | 3000 | leakage
Corroded | 0.8 | 4380 hours (1/2 year) | 4380 | dangerous
Painted | 0.9 | 5000 hours | 5000 | other
Non metallic | 0.9 | 6000 hours | 6000
Free input |  | 7000 hours | 7000
|  | 8760 hours (full year) | 8760
free input
General value ε=0,8
Metallic bright ε=0,3
Metallic ε=0,6
Corroded ε=0,8
Painted ε=0,9
Non metallic ε=0,9
Free input

## Warning list
Criteria |  | Warning | Advise | Action | Surface | Pipe | Flange | Valve | I Surface | I Pipe
Work flow
If component/location field is empty | ok | Please input Component/ Location |  | no calculation | x | x | x | x | x | x
If operational time is empty | revisar texto | Please input Operational time |  | no calculation | x | x | x | x | x | x
If surface is empty | revisar texto | Please input Surface in m² |  | no calculation | x |  |  |  | x
If Length is empty | revisar texto | Please input Length |  | no calculation |  | x |  |  |  | x
If Diameter (mm) is empty | revisar texto | Please input Diameter (mm) |  | no calculation |  | x | x | x |  | x
If Items number of items is empty | revisar texto | Please input Number of items |  | no calculation |  |  | x | x
If surface material is empty | revisar texto | Please input Surface emissivity |  | no calculation | x | x | x | x | x | x
If ambient temperature is empty | ok | Please input Ambient temperature |  | no calculation | x | x | x | x | x | x
If surface temperature is empty | revisar texto | Please input Surface temperature |  | no calculation | x | x | x | x | x | x
If medium temperature is empty | revisar texto | Please input Medium temperature |  | no calculation |  |  |  |  | x | x
If surface temperature < medium temperature & < ambient temp | funciona mal (surf temp menor que medium y menor que ambient | Please check temperatures |  | no calculation
If surface temperature > "Safety warning for θse" default value | funciona mal, safety warning = 55°C |  | "SAFETY - Insulation required" | indicate Hot Surface in the summary (safety) | x | x | x | x | x | x
If medium temp - surface temp < 15 °C (absolute value) | revisar texto | It is an un-insulated system, change selection |  | no calculation |  |  |  |  | x | x
If savings < 0 |  |  | System ok | no mostrar columnas de basic and good insualtion |  |  |  |  | x | x
Surface Material >1 or <0 | ok | Surface material emissivity must be between 0 and 1 |  | no calculation | x | x | x | x | x | x
Operational time >8760 or <0 | ok | Operational time must be between 0 and 8760 hours |  | no calculation | x | x | x | x | x | x
ABS( Surface Material - Ambient temperature) < 5 (el valor absoluto de la diferencia de temperaturas menor de 5 °C) |  | Surface temperature must be at least 5°C diferent than ambient temperature |  | no calculation | x | x | x | x | x | x
Diameter =< 0 | ok | Diameter must be > 0mm |  | no calculation |  | x | x | x |  | x
Length =< 0 |  | Length must be > 0 m |  | no calculation |  | x | x | x |  | x
Numbers of items =<0 |  | Number of items must be > 0 |  | no calculation |  |  | x | x
Surface =< 0 |  | Surface must be > 0 m |  | no calculation | x |  |  |  | x
Energy cost =< 0 |  | energy cost must be > 0 |  | no saved project
CO2 =< 0 |  | CO2 emission must be > 0 |  | no saved project
surface temperature > 999°C | ok | Surface temperarrure must be < 1000°C |  | no calculation | x | x | x | x | x
If surface temperature < ambient temperaure |  |  |  | report ficticio en others "Cold Surface" | x | x | x | x | x | x

## todo
information by selection
equivalent length
disclaimer about wind speed and sun radiation factor

## Andreas
inforamtion at the selection
DN or diameter
uninsulated others - only info per m2, no recommendation just conditional
Jacketing or cladding?
CO2 emission reduction?
Cold workflow
Limitation in temperatures, like up to 300 °C
Calculate or TIPCHECK?
Commmertialization
Bugs control with customers
round outputs ??